## A
Wire Sizer by Solarray, Inc. | Yellow boxes for User Input, check all yellow settings
Copyright 2008, all rights reserved | before double checking with your own final hand calculation
All calculations based on NEC 2005, chapter 9, table 8
Enter Operating Voltage | 66 | Volts (use array MPP voltage for MPPT controllers)
Enter Operating Current | 18 | amps
Wire distance | 85 | one way in feet
125% of PV short ciruit Amps | 22.5 | amps
Power | 1188 | watts
Wire Gauge | 18 | 14 | 12 | 10 | 8 | 6 | 4 | 2 | 1 | o | oo | oooo
Volts Lost | 20.7303 | 8.3182 | 5.2412 | 3.2855 | 2.0496 | 1.3299 | 0.83703 | 0.52412 | 0.41721 | 0.33116 | 0.26337 | 0.16323
Voltage drop | 31.41% | 12.6% | 7.941% | 4.978% | 3.105% | 2.015% | 1.268% | 0.7941% | 0.6321% | 0.5018% | 0.399% | 0.2473%
Final Voltage | 45.2697 | 57.6818 | 60.7588 | 62.7145 | 63.9504 | 64.6701 | 65.163 | 65.4759 | 65.5828 | 65.6688 | 65.7366 | 65.8368
Power lost (watts) | 373.1446 | 149.7272 | 94.3422 | 59.1399 | 36.892 | 23.9376 | 15.0666 | 9.4342 | 7.5098 | 5.9609 | 4.7406 | 2.9382
Efficiency | 68.59% | 87.4% | 92.06% | 95.02% | 96.89% | 97.99% | 98.73% | 99.21% | 99.37% | 99.5% | 99.6% | 99.75%
Cost of Lost power | 2985.1564 | 1197.8175 | 754.7377 | 473.1191 | 295.1362 | 191.5006 | 120.5327 | 75.4738 | 60.0786 | 47.6874 | 37.9246 | 23.5058
Pick a Gauge based on:
NEC 156% current (PV only) | go bigger | go bigger | go bigger | OK | OK | OK | OK | OK | OK | OK | OK | OK
very conservative
125% NEC load current | go bigger | go bigger | go bigger | OK | OK | OK | OK | OK | OK | OK | OK | OK
Normal Code, 24 hour cont. rating
Electric Vehicle, 1 hr rating | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
to not melt insulation
Cost effectiveness | go bigger | go bigger | go bigger | go bigger | go bigger | go bigger | OK | over sized | over sized | over sized | over sized | over sized
is cost of larger wire worth power gains
Comparable Cost of wire(2 x distance + etc) | 25.5 | 42.5 | 61.7 | 88.3 | 95 | 180 | 233 | 321 | 391 | 530 | 797 | 1315
Cost of connectors, extra time,etc per circuit | 0 | 0 | 0.5 | 5 | 10 | 10 | 12 | 15 | 17 | 20 | 32 | 40
Cost of wire per ft. THHN single | 0.15 | 0.25 | 0.36 | 0.49 | 0.5 | 1 | 1.3 | 1.8 | 2.2 | 3 | 4.5 | 7.5
weight of wire per 1000 ft | 4.92 | 12.4 | 19.8 | 31.4 | 50 | 79.5 | 126 | 201 | 253 | 319 | 403 | 641
resistance of wire per 1000 ft.@167 degF | 7.95 | 3.19 | 2.01 | 1.26 | 0.786 | 0.51 | 0.321 | 0.201 | 0.16 | 0.127 | 0.101 | 0.0626
NEC ampacity of THHN | 14 | 25 | 30 | 40 | 55 | 75 | 95 | 130 | 150 | 170 | 195 | 260
NEC Temp Compensated Ampacity | 14 | 25 | 30 | 40 | 55 | 75 | 95 | 130 | 150 | 170 | 195 | 260
(80%rated) normal breaker size | 15 | 15 | 20 | 30 | 40 | 60 | 100 | 125 | 150 | 175 | 200 | 250
max. ampacity | 18 | 35 | 40 | 55 | 80 | 105 | 140 | 190 | 220 | 260 | 300 | 400
Advanced User Inputs:
Temperature of wire in degrees F | 85 |  |  | Temperature Coefficient (Ohms) |  | 0.85215
Temperature of Air in degrees F | 85 |  |  | Temperature Coefficient (Amps) |  | 1
Cost of Copper per lb. | 1
Installed Cost of PV per watt | 8 | Used in cost of lost power calc.
Hours/ day at selected current | 6 | set to 6 for PV wiring, set to 1 for inverter rating, set to 0.5 for surge calculations, set to 24 for continuous loads, etc .
MPPT controller? | 1 | set to 0 for PV w/o MPPT , set to 1 for MPPT or for Non PV circuits also.